## Sheet1
| STRUCTURE NUMBER | SEGMENT | PROPOSED FACILITY ID (X/Y) | EXISTING FACILITY ID (X/Y) | EXISTING STRUCTURE CONFIGURATION DESCRIPTION | EXISTING STRUCTURE MATERIAL | EXISTING STRUCTURE HEIGHT (FT) | PROPOSED SURVEY COORD. X | PROPOSED SURVEY COORD. Y | OFFSET FROM EXISTING POLE LOCATION (FT) | NEW POLE STATION (FT) | OFFSET FROM CENTERLINE (FT) | AHEAD SPAN (FT) | LINE ANGLE (DEG.) | NEW STRUCTURE TYPE | NEW STRUCTURE CONFIGURATION DESCRIPTION | NEW STRUCTURE MATERIAL | TOTAL POLE LENGTH (FT) | POLE CLASS (NOTE 1) | STRUCTURE FRAMING DRAWING NO. | ACCESS TYPE (VEH/HELI) | FOUNDATION TYPE | FOUNDATION DRAWING NO. | FOUNDATION REVEAL (FT) | POLE EMBEDMENT (FT) (NOTE 2) | POLE HT. ABOVE GROUND (FT) | STR. HT ABOVE GROUND W/ REVEAL & INSULATOR (FT) | BIRD FLIGHT DIVERTERS REQ'D AHEAD SPAN (Y/N) | STRUCTURE IN WETLAND (Y/N) | DISTRIBUTION UNDERBUILD (Y/N) | DISTRIBUTION CONFIGURATION | PULLING LOCATION | STRUCTURE REMARKS / AHEAD SPAN COMMENTS | xm | ym | geometry | lat | lon | min_distance
0 | S4-1 | 4 | TBD | 736483-725881 | DEADEND RISER | WOOD | 51 | 1010244.269 | 14229256.068 | 5FT AHEAD | 0+00.00 | 0 | 141 | 0 | RISER | SC DEADEND RISER | GALVANIZED STEEL | 85 FT | -- | TS-4-301 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 86.5 | TBD | TBD | Y | DEAD END | TBD | ADSS SPLICE CUSTOM DISTRIBUTION DAVIT ARMS | 307923.069 | 4337085.9237 | POINT (-77.22314790584257 39.16180035311033) | 39.1618 | -77.2231 | 2.407
1 | S4-2 | 4 | TBD | 736483-845808 | TANGENT | WOOD | 64 | 1010363.256 | 14229180.611 | 65FT AHEAD | 1+40.90 | 0 | 129 | -8.5 | DEADEND | SC DEADEND | GALVANIZED STEEL | 90 FT | -- | TS-4-112 | VEH | DRILLED PIER | TBD | 1.5 | -- | 90 | 91.5 | TBD | TBD | Y | DEAD END | TBD |  | 307959.3363 | 4337062.9244 | POINT (-77.22272191346221 39.16160126511792) | 39.1616 | -77.2227 | 7.1968
2 | S4-3 | 4 | TBD | 736483-880720 | TANGENT | WOOD | 60 | 1010481.166 | 14229128.4 | 5FT BACK | 2+69.85 | 0 | 192 | 7.06 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 110 FT | LD CL H10 | TS-4-114 | VEH | DIRECT EMBED | TBD | -- | 19 | 91 | 91 | TBD | TBD | Y | -- | TBD |  | 307995.2754 | 4337047.0104 | POINT (-77.22230172852845 39.1614659021706) | 39.1615 | -77.2223 | 3.118
3 | S4-4 | 4 | TBD | 737483-131664 | DEADEND | WOOD | 54 | 1010645.52 | 14229029.865 | 5FT BACK | 4+61.48 | 0 | 175 | 0 | DEADEND | SC DEADEND | GALVANIZED STEEL | 90 FT | -- | TS-4-112 | VEH | DRILLED PIER | TBD | 1.5 | -- | 90 | 91.5 | TBD | TBD | Y | DEAD END | TBD |  | 308045.3706 | 4337016.9769 | POINT (-77.22171381325688 39.16120652347538) | 39.1612 | -77.2217 | 3.0905
4 | S4-5 | 4 | TBD | 737483-200540 | TANGENT | WOOD | 53 | 1010795.361 | 14228940.031 | 5FT BACK | 6+36.18 | 0 | 219 | 1.68 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 308091.0422 | 4336989.5954 | POINT (-77.22117781652757 39.16097004616433) | 39.161 | -77.2212 | 0.89371
5 | S4-6 | 4 | TBD | 737483-390430 | TANGENT | WOOD | 57 | 1010979.409 | 14228822.199 | 5FT AHEAD | 8+54.72 | 0 | 189 | 2.9 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 308147.1402 | 4336953.6802 | POINT (-77.22051881609204 39.16065902397973) | 39.1607 | -77.2205 | 2.5192
6 | S4-7 | 4 | TBD | 737483-623353 | TANGENT | WOOD | 50 | 1011132.836 | 14228712.667 | 5FT BACK | 10+43.23 | 0 | 143 | 8.25 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 110 FT | LD CL H10 | TS-4-114 | VEH | DIRECT EMBED | TBD | -- | 19 | 91 | 91 | TBD | TBD | Y | -- | TBD |  | 308193.9048 | 4336920.2947 | POINT (-77.21996848570296 39.16036872018847) | 39.1604 | -77.22 | 0.67684
7 | S4-8 | 4 | TBD | 737483-710120 | TANGENT | WOOD | 60 | 1011236.316 | 14228613.54 | 5FT AHEAD | 11+86.53 | 0 | 221 | 9.37 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 120 FT | LD CL V14 | TS-4-114 | VEH | DIRECT EMBED | TBD | -- | 19.5 | 100.5 | 100.5 | TBD | TBD | Y | -- | TBD |  | 308225.4456 | 4336890.0808 | POINT (-77.21959513485606 39.16010361542229) | 39.1601 | -77.2196 | 0.1588
8 | S4-9 | 4 | TBD | 737483-861084 | TANGENT | WOOD | 61 | 1011368.652 | 14228437.031 | 10FT BACK, OFFSET 10FT | 14+07.14 | 0 | 169 | 14 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 95 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 95 | 96.5 | TBD | TBD | Y | -- | TBD |  | 308265.7817 | 4336836.2807 | POINT (-77.21911338626157 39.1596280703878) | 39.1596 | -77.2191 | 2.3947
9 | S4-10 | 4 | TBD | 737482-936932 | DEADEND TAP | WOOD | 54 | 1011434.396 | 14228281.08 | 5FT AHEAD | 15+76.38 | 0 | 230 | -2.65 | DEADEND TAP | SC DEADEND | GALVANIZED STEEL | 100 FT | -- | TS-4-112 | VEH | DRILLED PIER | TBD | 1.5 | -- | 100 | 101.5 | TBD | TBD | Y | DEAD END | TBD | ADSS SPLICE 69kV TAP TO LOCKHEED MARTIN SUB | 308285.8205 | 4336788.7468 | POINT (-77.21886817007325 39.15920447365639) | 39.1592 | -77.2189 | 1.1383
10 | S4-11 | 4 | TBD | 738482-014779 | TANGENT | WOOD | 63 | 1011508.448 | 14228125.898 | 5FT BACK | 17+48.33 | 0 | 225 | -6.52 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL V14 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 308308.3916 | 4336741.4472 | POINT (-77.21859373571451 39.15878354465841) | 39.1588 | -77.2186 | 1.7038
11 | S4-12 | 4 | TBD | 738482-124577 | DEADEND SWITCH | WOOD | 57 | 1011627.847 | 14227935.079 | 5FT BACK | 19+73.42 | 0 | 223 | -2.39 | DEADEND SWITCH | SC DEADEND SWITCH | GALVANIZED STEEL | 85 FT | -- | TBD | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 86.5 | TBD | TBD | Y | DEAD END | TBD | LIGHTNING ARRESTERS (LADEKV) TO BE INSTALLED AT EACH 69KV DEAD END ASSEMBLY FOR THIS STRUCTURE. SWITCH GROUNDING MAT TO BE INSTALLED BELOW SWITCH HANDLE, PER CONECTIV STANDARD 11-12. | 308344.7845 | 4336683.2854 | POINT (-77.21815637474235 39.15826785228168) | 39.1583 | -77.2182 | 5.8105
12 | S4-13 | 4 | TBD | 738482-267410 | TANGENT | WOOD | 61 | 1011754.025 | 14227750.997 | 5FT AHEAD | 21+96.60 | 0 | 212 | -0.15 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 308383.2436 | 4336627.1771 | POINT (-77.21769570387772 39.15777110290283) | 39.1578 | -77.2177 | 3.9635
13 | S4-14 | 4 | TBD | 738482-391238 | TANGENT | WOOD | 65 | 1011874.153 | 14227576.718 | 5FT AHEAD | 24+08.27 | 0 | 202 | 1.02 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 95 FT | LD CL H9 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 79 | 83.5 | TBD | TBD | Y | -- | TBD |  | 308419.8587 | 4336574.0568 | POINT (-77.21725721159108 39.15730085016754) | 39.1573 | -77.2173 | 2.7558
14 | S4-15 | 4 | TBD | 738482-506072 | TANGENT | WOOD | 60 | 1011985.668 | 14227408.602 | 5FT BACK | 26+10.01 | 0 | 148 | -1.62 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 90 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15 | 75 | 79.5 | TBD | TBD | Y | -- | TBD |  | 308453.8485 | 4336522.8149 | POINT (-77.21684961818681 39.15684693231825) | 39.1568 | -77.2168 | 5.2248
15 | S4-16 | 4 | TBD | 738481-594954 | TANGENT | WOOD | 60 | 1012070.728 | 14227287.912 | 5FT BACK | 27+57.66 | 0 | 158 | 0.63 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 90 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15 | 75 | 79.5 | TBD | TBD | Y | -- | TBD |  | 308479.7749 | 4336486.0285 | POINT (-77.21653937271741 39.15652140062092) | 39.1565 | -77.2165 | 6.2425
18 | S4-19 | 4 | TBD | 738481-946570 | TANGENT | WOOD | 60 | 1012413.944 | 14226896.149 | 5FT BACK | 32+80.07 | 0 | 231 | 3.75 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16.5 | 83.5 | 88 | TBD | TBD | Y | -- | TBD |  | 308584.3873 | 4336366.6189 | POINT (-77.2152957642711 39.1554692086275) | 39.1555 | -77.2153 | 1.8147
20 | S4-21 | 4 | TBD | 739481-180180 | TANGENT | WOOD | 59 | 1012731.004 | 14226532.331 | 5FT AHEAD | 37+62.80 | 0 | 270 | -3.17 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 85 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 91 | TBD | TBD | Y | -- | TBD |  | 308681.0274 | 4336255.727 | POINT (-77.21414679806598 39.15449194579092) | 39.1545 | -77.2141 | 4.7891
21 | S4-21A | 4 | -- | 739481-260090 | TANGENT | WOOD | 58 | 1012797.084 | 14226467.636 | EX. TO REM. | 38+55.28 | 0 | 178 | 3.08 | DIST. INSET | -- | -- | -- | -- | -- | VEH | -- | -- | -- | -- | 57 | 56.5 | TBD | TBD | -- | DEAD END | TBD |  | 308701.1686 | 4336236.0079 | POINT (-77.21390829819977 39.15431881506426) | 39.1543 | -77.2139 | 0.51464
22 | S4-22 | 4 | TBD | 739480-350980 | TANGENT | WOOD | 55 | 1012917.341 | 14226336.51 | 15FT BACK | 40+33.20 | 0 | 146 | 1.81 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 18 | 82 | 86.5 | TBD | TBD | Y | -- | TBD |  | 308737.823 | 4336196.0406 | POINT (-77.21347311061112 39.1539669902479) | 39.154 | -77.2135 | 1.1525
23 | S4-23 | 4 | TBD | 739480-450870 | TANGENT | WOOD | 56 | 1013012.862 | 14226225.516 | 5FT AHEAD | 41+79.64 | 0 | 134 | -3.16 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 308766.9379 | 4336162.2096 | POINT (-77.2131268527741 39.15366876023587) | 39.1537 | -77.2131 | 2.9458
24 | S4-24 | 4 | TBD | 739480-540770 | TANGENT | WOOD | 58 | 1013105.56 | 14226129.095 | 5FT AHEAD | 43+13.39 | 0 | 134 | 2.67 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 85 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 91 | TBD | TBD | Y | -- | TBD |  | 308795.1923 | 4336132.8204 | POINT (-77.21279180211235 39.15341033627691) | 39.1534 | -77.2128 | 0.68
25 | S4-25 | 4 | TBD | 739480-640680 | TANGENT | WOOD | 59 | 1013193.718 | 14226028.418 | 5FT AHEAD | 44+47.21 | 0 | 158 | -5.98 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 100 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 100 | 101.5 | TBD | TBD | Y | DEAD END | TBD | ADSS SPLICE | 308822.0629 | 4336102.134 | POINT (-77.2124723912378 39.15313992655303) | 39.1531 | -77.2125 | 1.9161
28 | S4-27 | 4 | TBD | 739480-960330 | TANGENT | WOOD | 56 | 1013491.747 | 14225725.29 | 5FT AHEAD, OFFSET 10FT | 48+73.16 | 0 | 150 | 10.57 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 125 FT | LD CL V14 | TS-4-114 | VEH | DIRECT EMBED | TBD | -- | 20.5 | 104.5 | 104.5 | TBD | TBD | Y | -- | TBD |  | 308912.9023 | 4336009.7404 | POINT (-77.21139580052828 39.15232792626953) | 39.1523 | -77.2114 | 0.33797
29 | S4-28 | 4 | TBD | 740480-040270 | TANGENT | WOOD | 59 | 1013581.492 | 14225604.491 | 5FT AHEAD | 50+23.67 | 0 | 192 | -7.3 | DEADEND | SC DEADEND | GALVANIZED STEEL | 100 FT | -- | TS-4-112 | VEH | DRILLED PIER | TBD | 1.5 | -- | 100 | 101.5 | TBD | TBD | Y | DEAD END | TBD | ADSS SPLICE | 308940.2566 | 4335972.9208 | POINT (-77.21106907684869 39.15200239280965) | 39.152 | -77.2111 | 4.3874
30 | S4-29 | 4 | TBD | 740480-170120 | TANGENT | WOOD | 63 | 1013714.705 | 14225465.88 | 5FT BACK, OFFSET 10FT | 52+15.92 | 0 | 103 | 5.1 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 125 FT | LD CL H10 | TS-4-114 | VEH | DIRECT EMBED | TBD | -- | 20.5 | 104.5 | 104.5 | TBD | TBD | Y | -- | TBD |  | 308980.86 | 4335930.6721 | POINT (-77.21058760632181 39.15163088013944) | 39.1516 | -77.2106 | 1.3422
31 | S4-30 | 4 | TBD | 740480-230060 | TANGENT | WOOD | 64 | 1013778.877 | 14225385.95 | 10FT AHEAD | 53+18.40 | 0 | 151 | -3.92 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 110 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 17 | 93 | 97.5 | TBD | TBD | Y | -- | TBD |  | 309000.4197 | 4335906.3094 | POINT (-77.21035454163528 39.15141580072907) | 39.1514 | -77.2104 | 0.492
32 | S4-31 | 4 | TBD | 740479-360930 | TANGENT | WOOD | 60 | 1013881.239 | 14225274.943 | 5FT BACK | 54+69.42 | 0 | 212 | 0.52 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 105 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 89 | 93.5 | TBD | TBD | Y | -- | TBD |  | 309031.6197 | 4335872.4744 | POINT (-77.20998419488541 39.15111798237213) | 39.1511 | -77.21 | 1.9344
33 | S4-32 | 4 | TBD | 740479-594827 | TANGENT | WOOD | 55 | 1014023.668 | 14225117.63 | 5FT AHEAD | 56+81.63 | 0 | 203 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H9 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 309075.0322 | 4335824.5253 | POINT (-77.2094686453827 39.15069575240841) | 39.1507 | -77.2095 | 2.0259
35 | S4-34 | 4 | TBD | 740479-780500 | TANGENT | WOOD | 60 | 1014281.059 | 14224830.548 | 5FT BACK | 60+67.21 | 0 | 169 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 95 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15.5 | 79.5 | 84 | TBD | TBD | Y | -- | TBD |  | 309153.4851 | 4335737.0225 | POINT (-77.20853674447099 39.149925045488) | 39.1499 | -77.2085 | 0.48083
36 | S4-35 | 4 | TBD | 740479-870380 | TANGENT | WOOD | 57 | 1014393.141 | 14224704.173 | 5FT BACK | 62+36.10 | 0 | 164 | -3.97 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 90 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15 | 75 | 79.5 | TBD | TBD | Y | -- | TBD |  | 309187.6478 | 4335698.5033 | POINT (-77.20813083361541 39.14958569198318) | 39.1496 | -77.2081 | 0.92672
37 | S4-36 | 4 | TBD | 740479-990260 | TANGENT | WOOD | 59 | 1014510.357 | 14224589.152 | 5FT BACK, OFFSET 10FT | 64+00.33 | 0 | 198 | 4.9 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 95 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 17.5 | 77.5 | 82 | TBD | TBD | Y | -- | TBD |  | 309223.3753 | 4335663.4449 | POINT (-77.20770780454899 39.1492778415374) | 39.1493 | -77.2077 | 4.6043
38 | S4-37 | 4 | TBD | 741479-120110 | TANGENT | WOOD | 54 | 1014639.532 | 14224438.635 | 5FT BACK | 65+98.70 | 0 | 127 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 309262.7479 | 4335617.5672 | POINT (-77.20723958209743 39.14887336743154) | 39.1489 | -77.2072 | 0.69394
40 | S4-39 | 4 | TBD | 741478-350870 | TANGENT | WOOD | 55 | 1014854.769 | 14224181.447 | 10FT AHEAD | 69+34.06 | 0 | 152 | 3.31 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 309328.3522 | 4335539.1761 | POINT (-77.20645887359467 39.14818187271383) | 39.1482 | -77.2065 | 5.707
41 | S4-40 | 4 | TBD | 741478-450740 | TANGENT | WOOD | 55 | 1014944.669 | 14224058.521 | 5FT BACK | 70+86.35 | 0 | 289 | -4.91 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 309355.7538 | 4335501.7082 | POINT (-77.20613146345265 39.14785049665899) | 39.1479 | -77.2061 | 1.1842
42 | S4-40A | 4 | -- | 741478-560630 | TANGENT | WOOD | 55 | 1015051.739 | 14223935.75 | EX. TO REM. | 72+49.28 | 0 | 126 | -0.48 | DIST. INSET | -- | -- | -- | -- | -- | VEH | -- | -- | -- | -- | 54 | 54 | TBD | TBD | -- | DEAD END | TBD |  | 309388.3888 | 4335464.2875 | POINT (-77.20574355078917 39.14752069088303) | 39.1475 | -77.2057 | 0.76997
43 | S4-41 | 4 | TBD | 741478-640530 | TANGENT | WOOD | 54 | 1015135.49 | 14223841.312 | 5FT BACK | 73+75.50 | 0 | 124 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 105 FT | LD CL H6 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16.5 | 88.5 | 93 | TBD | TBD | Y | -- | TBD |  | 309413.9162 | 4335435.5028 | POINT (-77.20544026160881 39.14726708926452) | 39.1473 | -77.2054 | 1.2405
44 | S4-42 | 4 | TBD | 741478-720440 | TANGENT | WOOD | 54 | 1015218.077 | 14223748.185 | 5FT BACK | 74+99.97 | 0 | 124 | -0.41 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H7 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 309439.0887 | 4335407.1176 | POINT (-77.20514118965295 39.14701700723972) | 39.147 | -77.2051 | 1.705
45 | S4-43 | 4 | TBD | 741478-810350 | TANGENT | WOOD | 54 | 1015301 | 14223656.011 | 5FT BACK | 76+23.96 | 0 | 213 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 95 FT | LD CL H6 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15.5 | 79.5 | 84 | TBD | TBD | Y | -- | TBD |  | 309464.3637 | 4335379.0229 | POINT (-77.20484101718117 39.1467695623557) | 39.1468 | -77.2048 | 1.2842
46 | S4-43A | 4 | -- | 741478-890250 | TANGENT | WOOD | 52 | 1015381.211 | 14223566.851 | EX. TO REM. | 77+43.89 | 0 | 93 | -0.94 | DIST. INSET | -- | -- | -- | -- | -- | VEH | -- | -- | -- | -- | 50.5 | 50.5 | TBD | TBD | -- | DEAD END | TBD |  | 309488.8121 | 4335351.8469 | POINT (-77.20455066382054 39.14653020784223) | 39.1465 | -77.2046 | 0.68829
47 | S4-44 | 4 | TBD | 741478-960190 | TANGENT | WOOD | 55 | 1015444.462 | 14223498.815 | 5FT AHEAD | 78+36.78 | 0 | 130 | 1.61 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 95 FT | LD CL H6 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15.5 | 79.5 | 84 | TBD | TBD | Y | -- | TBD |  | 309508.091 | 4335331.1095 | POINT (-77.20432189941626 39.14634769754612) | 39.1463 | -77.2043 | 1.1714
53 | S4-50 | 4 | TBD | 742477-520580 | TANGENT | WOOD | 53 | 1016003.878 | 14222875.183 | 5FT AHEAD | 86+74.59 | 0 | 232 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 95 FT | LD CL H7 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15.5 | 79.5 | 84 | TBD | TBD | Y | -- | TBD |  | 309678.6014 | 4335141.0261 | POINT (-77.20229679768737 39.14467339152634) | 39.1447 | -77.2023 | 0.004905
54 | S4-50A | 4 | -- | 742477-600500 | TANGENT | WOOD | 55 | 1016076.001 | 14222795.622 | EX. TO REM. | 87+81.98 | 0 | 125 | 0.32 | DIST. INSET | -- | -- | -- | -- | -- | VEH | -- | -- | -- | -- | 44 | 43.8 | TBD | TBD | -- | DEAD END | TBD |  | 309700.5845 | 4335116.7758 | POINT (-77.2020357893515 39.14445983635596) | 39.1445 | -77.202 | 0.10621
55 | S4-51 | 4 | TBD | 742477-700400 | TANGENT | WOOD | 49 | 1016159.323 | 14222702.667 | 5FT BACK | 89+06.81 | 0 | 107 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H6 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 16 | 84 | 88.5 | TBD | TBD | Y | -- | TBD |  | 309725.9811 | 4335088.4431 | POINT (-77.20173416558129 39.14421026581569) | 39.1442 | -77.2017 | 0.92245
56 | S4-52 | 4 | TBD | 742477-856382 | DEADEND | WOOD | 57 | 1016230.874 | 14222622.843 | 5FT AHEAD | 90+14.01 | 0 | 72 | -1.74 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 105 FT | LD CL H7 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 18.5 | 86.5 | 91 | TBD | TBD | Y | -- | TBD |  | 309747.7899 | 4335064.1127 | POINT (-77.20147515419823 39.14399594935261) | 39.144 | -77.2015 | 1.622
58 | S4-54 | 4 | TBD | 742477-960130 | TANGENT | WOOD | 59 | 1016410.675 | 14222426.751 | 5FT AHEAD | 92+80.07 | 0 | 195 | 0.5 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 85 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 91 | TBD | TBD | Y | -- | TBD |  | 309802.5933 | 4335004.3437 | POINT (-77.20082467428824 39.14346973509873) | 39.1435 | -77.2008 | 0.045019
59 | S4-54A | 4 | -- | 742477-990090 | TANGENT | WOOD | 58 | 1016457.21 | 14222373.904 | EX. TO REM. | 93+50.50 | 0.3 | 124 | 4.46 | DIST. INSET | -- | -- | -- | -- | -- | VEH | -- | -- | -- | -- | 58 | 56.5 | TBD | TBD | -- | DEAD END | TBD |  | 309816.7772 | 4334988.2359 | POINT (-77.20065614344716 39.14332779119521) | 39.1433 | -77.2007 | 0.59097
60 | S4-55 | 4 | TBD | 743476-090980 | TANGENT | WOOD | 48 | 1016532.531 | 14222274.979 | 5FT BACK | 94+74.84 | 0 | 94 | -3.34 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 95 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 95 | 96.5 | TBD | TBD | Y | -- | TBD |  | 309839.7351 | 4334958.0835 | POINT (-77.20038221842573 39.14306129906313) | 39.1431 | -77.2004 | 3.8879
61 | S4-56 | 4 | TBD | 743476-228971 | TANGENT | WOOD | 60 | 1016593.569 | 14222203.486 | 10FT BACK | 95+68.85 | 0 | 173 | 5.16 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 95 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 95 | 96.5 | TBD | TBD | Y | -- | TBD |  | 309858.3395 | 4334936.2924 | POINT (-77.20016098023214 39.1428691445679) | 39.1429 | -77.2002 | 6.7523
65 | S4-60 | 4 | TBD | 743476-520470 | TANGENT | WOOD | 59 | 1016929.263 | 14221748.959 | 30FT BACK, OFFSET 20FT | 101+35.33 | 0 | 171 | -19.74 | DEADEND | SC DEADEND | GALVANIZED STEEL | 100 FT | -- | TS-4-112 | VEH | DRILLED PIER | TBD | 1.5 | -- | 100 | 101.5 | TBD | TBD | Y | DEAD END | TBD |  | 309960.6593 | 4334797.7523 | POINT (-77.19893900672592 39.14164400076098) | 39.1416 | -77.1989 | 3.0446
66 | S4-61 | 4 | TBD | 743476-729453 | DEADEND | WOOD | 55 | 1017083.527 | 14221675.011 | 10FT AHEAD, OFFSET 5FT | 103+06.40 | 0 | 233 | 12.48 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 95 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 95 | 96.5 | TBD | TBD | Y | -- | TBD |  | 310007.679 | 4334775.2129 | POINT (-77.19838900123344 39.14145130591182) | 39.1415 | -77.1984 | 0.2106
72 | S4-66 | 4 | TBD | 744475-373828 | DEADEND RISER | WOOD | 57 | 1017713.474 | 14221035.914 | 5FT AHEAD | 112+08.12 | 0 | 46 | 0 | RISER | SC DEADEND RISER | GALVANIZED STEEL | 85 FT | -- | TS-4-301 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 86.6 | TBD | TBD | Y | DEAD END | TBD | ADSS SPLICE CUSTOM DISTRIBUTION DAVIT ARMS | 310199.6873 | 4334580.4157 | POINT (-77.1961142876691 39.13973912849481) | 39.1397 | -77.1961 | 2.1113
78 | S5-6 | 5 | TBD | 735484-600600 | TANGENT | WOOD | 63 | 1009213.623 | 14230024.357 | 5FT BACK | 9+41.84 | 0 | 175 | 2.76 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 100 | 106 | TBD | TBD | Y | -- | TBD |  | 307608.9275 | 4337320.0987 | POINT (-77.22684781071611 39.16383952797881) | 39.1638 | -77.2268 | 6.0268
89 | S5-17 | 5 | TBD | 734486-474099 | TANGENT | WOOD | 51 | 1008042.67 | 14231523.694 | 5FT AHEAD | 28+77.38 | 0 | 151 | -4.48 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 100 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 18 | 82 | 86.5 | TBD | TBD | Y | -- | TBD |  | 307252.0203 | 4337777.0975 | POINT (-77.23110600437136 39.16787546683484) | 39.1679 | -77.2311 | 5.9959
90 | S5-18 | 5 | TBD | 734486-330147 | TANGENT | WOOD | 47 | 1007900.172 | 14231574.667 | 5FT AHEAD | 30+28.72 | 0 | 201 | -7.13 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 85 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 86.5 | TBD | TBD | Y | -- | TBD |  | 307208.5868 | 4337792.6341 | POINT (-77.23161282468605 39.16800573771901) | 39.168 | -77.2316 | 1.4528
95 | S5-23 | 5 | TBD | 733486-420480 | DEADEND | WOOD | 49 | 1007085.586 | 14231946.694 | 5FT BACK | 39+45.12 | 0 | 233 | 9 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 85 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 86.5 | TBD | TBD | Y | DEADEND | TBD |  | 306960.3005 | 4337906.0281 | POINT (-77.23451709053944 39.16897170360035) | 39.169 | -77.2345 | 5.3836
99 | S5-27 | 5 | TBD | 733487-063220 | TANGENT | WOOD | 50 | 1006720.84 | 14232690.521 | 5FT BACK | 47+76.19 | 0 | 140 | 1.24 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 75 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 75 | 81 | TBD | TBD | Y | -- | TBD |  | 306849.1257 | 4338132.7471 | POINT (-77.23586774377901 39.17098845204382) | 39.171 | -77.2359 | 4.0929
100 | S5-28 | 5 | TBD | 733487-073366 | TANGENT | WOOD | 50 | 1006670.337 | 14232821.139 | 5FT AHEAD | 49+16.23 | 0 | 156 | -1.39 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 95 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 17.5 | 77.5 | 82 | TBD | TBD | Y | -- | TBD |  | 306833.7324 | 4338172.5595 | POINT (-77.23605716487663 39.17134351353111) | 39.1713 | -77.2361 | 1.249
101 | S5-29 | 5 | TBD | 732487-940480 | TANGENT | WOOD | 50 | 1006610.647 | 14232965.03 | 5FT AHEAD | 50+72.01 | 0 | 226 | 0.31 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 80 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 80 | 86 | TBD | TBD | Y | -- | TBD |  | 306815.5388 | 4338216.4176 | POINT (-77.23628013401382 39.17173438032396) | 39.1717 | -77.2363 | 7.9193
102 | S5-30 | 5 | TBD | 732487-921715 | TANGENT | WOOD | 49 | 1006525.259 | 14233174.015 | 5FT AHEAD | 52+97.77 | 0 | 224 | -1.17 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 80 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 80 | 86 | TBD | TBD | Y | -- | TBD |  | 306789.5125 | 4338280.1163 | POINT (-77.23659937483596 39.17230215645009) | 39.1723 | -77.2366 | 2.9046
103 | S5-31 | 5 | TBD | 732487-827919 | TANGENT | WOOD | 49 | 1006436.133 | 14233380.053 | 5FT AHEAD | 55+22.26 | 0 | 227 | 1.45 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 75 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 75 | 81 | TBD | TBD | Y | -- | TBD |  | 306762.3469 | 4338342.9168 | POINT (-77.23693154433154 39.17286159037009) | 39.1729 | -77.2369 | 2.9517
104 | S5-32 | 5 | TBD | 732488-680080 | TANGENT | WOOD | 58 | 1006351.389 | 14233590.411 | 5FT AHEAD | 57+49.04 | 0 | 224 | -1.82 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 75 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 75 | 81 | TBD | TBD | Y | -- | TBD |  | 306736.5168 | 4338407.0341 | POINT (-77.23724864462959 39.17343317610482) | 39.1734 | -77.2372 | 5.7054
106 | S5-34 | 5 | TBD | 732488-575491 | TANGENT | WOOD | 54 | 1006197.086 | 14233957.479 | 5FT BACK | 61+47.30 | 0 | 190 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 90 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15 | 75 | 79.5 | TBD | TBD | Y | -- | TBD |  | 306689.4852 | 4338518.9166 | POINT (-77.23782465008227 39.17443013699695) | 39.1744 | -77.2378 | 4.7211
107 | S5-35 | 5 | TBD | 732488-502666 | TANGENT | WOOD | 50 | 1006127.288 | 14234134.153 | 5FT AHEAD | 63+37.26 | 0 | 225 | 0.38 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 90 FT | LD CL H8 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 15 | 75 | 79.5 | TBD | TBD | Y | -- | TBD |  | 306668.2107 | 4338572.767 | POINT (-77.23808613367382 39.17491028721536) | 39.1749 | -77.2381 | 4.8578
108 | S5-35A | 5 | -- | 732488-400750 | TANGENT | WOOD | 54 | 1006086.904 | 14234238.361 | EX. TO REM. | 64+49.02 | 0 | 113 | 3.83 | -- | -- | -- | 53.5 FT | -- | -- | VEH | -- | -- | -- | -- | 53.5 | 49.5 | TBD | TBD | -- | DEAD END | TBD |  | 306655.9017 | 4338604.5296 | POINT (-77.23823759855951 39.17519354809428) | 39.1752 | -77.2382 | 4.4951
109 | S5-36 | 5 | TBD | 732488-423877 | TANGENT | WOOD | 53 | 1006053.132 | 14234346.452 | 5FT AHEAD | 65+62.26 | 0 | 180 | 4.07 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 90 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 14.5 | 75.5 | 80 | TBD | TBD | Y | -- | TBD |  | 306645.6079 | 4338637.4758 | POINT (-77.23836608881079 39.17548791361735) | 39.1755 | -77.2384 | 7.9931
110 | S5-37 | 5 | TBD | 732489-320020 | TANGENT | WOOD | 54 | 1006011.784 | 14234521.653 | 5FT AHEAD | 67+42.28 | 0 | 178 | 4.04 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 90 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 14.5 | 75.5 | 80 | TBD | TBD | Y | -- | TBD |  | 306633.005 | 4338690.8772 | POINT (-77.23852713647906 39.17596594779121) | 39.176 | -77.2385 | 0.19161
114 | S5-41 | 5 | TBD | 732489-240650 | TANGENT | WOOD | 57 | 1005965.01 | 14235181.439 | 5FT AHEAD | 74+05.63 | 0 | 138 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 80 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 80 | 81 | TBD | TBD | Y | -- | TBD |  | 306618.7483 | 4338891.9804 | POINT (-77.23874951655019 39.17777354872882) | 39.1778 | -77.2387 | 2.5455
115 | S5-41A | 5 | -- | 732489-230710 | TANGENT | WOOD | 54 | 1005967.405 | 14235224.443 | EX. TO REM. | 74+48.70 | 0 | 95 | 0 | -- | -- | -- | 53 FT | -- | -- | VEH | -- | -- | -- | -- | 53 | 53 | TBD | TBD | -- | DEAD END | TBD |  | 306619.4783 | 4338905.088 | POINT (-77.2387448164056 39.17789173475019) | 39.1779 | -77.2387 | 2.6459
116 | S5-42 | 5 | TBD | 732489-321848 | DEADEND | WOOD | 62 | 1005972.684 | 14235319.225 | 5FT BACK | 75+43.63 | 0 | 58 | -56.34 | DEADEND | SC DEADEND | GALVANIZED STEEL | 80 FT | -- | TS-4-112 | VEH | DRILLED PIER | TBD | 1.5 | -- | 80 | 81.5 | TBD | TBD | Y | DEADEND | TBD | ADSS SPLICE | 306621.0873 | 4338933.9776 | POINT (-77.23873445588688 39.17815222001234) | 39.1782 | -77.2387 | 2.8676
117 | S5-43 | 5 | TBD | 732489-273882 | DEADEND | WOOD | 58 | 1005925.88 | 14235354.303 | 5FT BACK | 76+02.12 | 0 | 272 | -54.11 | DEADEND | SC DEADEND | GALVANIZED STEEL | 80 FT | -- | TS-4-112 | VEH | DRILLED PIER | TBD | 1.5 | -- | 80 | 81.5 | TBD | TBD | Y | DEADEND | TBD |  | 306606.8214 | 4338944.6694 | POINT (-77.23890254823631 39.17824531846552) | 39.1782 | -77.2389 | 6.6475
118 | S5-43A | 5 | -- | 732489-110820 | DEADEND | WOOD | 52 | 1005861.85 | 14235334.407 | EX. TO REM. | 76+69.17 | 0 | 205 | 0 | -- | -- | -- | 49 FT | -- | -- | VEH | -- | -- | -- | -- | 49 | 48 | TBD | TBD | -- | DEAD END | TBD |  | 306587.3051 | 4338938.6051 | POINT (-77.23912659424629 39.17818637381457) | 39.1782 | -77.2391 | 2.2548
119 | S5-44 | 5 | TBD | 732489-015795 | TANGENT | WOOD | 55 | 1005665.708 | 14235273.46 | 25FT AHEAD | 78+74.56 | 0 | 235 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 95 FT | LD CL H10 | TS-4-113 | VEH | DIRECT EMBED | TBD | -- | 17.5 | 77.5 | 82 | TBD | TBD | Y | DEAD END | TBD |  | 306527.5209 | 4338920.0284 | POINT (-77.23981290810508 39.17800580726452) | 39.178 | -77.2398 | 2.3957
120 | S5-45 | 5 | TBD | 731489-700680 | TANGENT | WOOD | 53 | 1005441.091 | 14235203.664 | 5FT AHEAD | 81+09.77 | 0 | 233 | 5.21 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 85 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 86.5 | TBD | TBD | Y | DEAD END | TBD |  | 306459.0575 | 4338898.7546 | POINT (-77.2405988532621 39.17779901931173) | 39.1778 | -77.2406 | 1.2333
121 | S5-46 | 5 | TBD | 731489-565667 | TANGENT | WOOD | 58 | 1005213.415 | 14235155.062 | 5 FT BACK, OFFSET 10FT | 83+42.58 | 0 | 227 | 2.56 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 80 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 80 | 86 | TBD | TBD | Y | DEAD END | TBD |  | 306389.6617 | 4338883.9407 | POINT (-77.24139742774679 39.17765018504127) | 39.1777 | -77.2414 | 3.381
122 | S5-47 | 5 | TBD | 731489-342624 | TANGENT | WOOD | 47 | 1004989.469 | 14235117.62 | 5FT BACK | 85+69.63 | 0 | 234 | -3.92 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 70 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 70 | 76 | TBD | TBD | Y | DEAD END | TBD |  | 306321.4028 | 4338872.5283 | POINT (-77.24218381959386 39.17753222693581) | 39.1775 | -77.2422 | 2.3246
123 | S5-47A | 5 | -- | 731489-170560 | TANGENT | WOOD | 51 | 1004905.079 | 14235097.499 | EX. TO REM. | 86+56.39 | 0 | 147 | -2.61 | -- | -- | -- | 50 FT | -- | -- | VEH | -- | -- | -- | -- | 50 | 49.7 | TBD | TBD | -- | DEAD END | TBD |  | 306295.6807 | 4338866.3954 | POINT (-77.24247963201378 39.17747127635028) | 39.1775 | -77.2425 | 1.2934
124 | S5-48 | 5 | TBD | 731489-020520 | TANGENT | WOOD | 54 | 1004763.628 | 14235056.884 | 10FT BACK | 88+03.56 | 0 | 175 | -7.49 | TANGENT | SC DELTA POST TANGENT | GALVANIZED STEEL | 85 FT | -- | TS-4-114 | VEH | DRILLED PIER | TBD | 1.5 | -- | 85 | 86.5 | TBD | TBD | Y | -- | TBD |  | 306252.5663 | 4338854.016 | POINT (-77.24297485819928 39.17735020513376) | 39.1774 | -77.243 | 2.0207
126 | S5-50 | 5 | TBD | 730489-710330 | TANGENT | WOOD | 53 | 1004434.334 | 14234874.216 | 5FT BACK | 91+81.63 | 0 | 222 | 0 | TANGENT | SC DELTA STAR TANGENT | GALVANIZED STEEL | 80 FT | -- | TS-4-113 | VEH | DRILLED PIER | TBD | 1.5 | -- | 80 | 86 | TBD | TBD | Y | -- | TBD |  | 306152.1973 | 4338798.3386 | POINT (-77.24412003235595 39.17682651096803) | 39.1768 | -77.2441 | 2.6546